## ALL LOADS
WORKSHEET - NEC 2014, 220 PART IV
Contractor |  |  |  | E-mail
Phone |  |  |  | Fax
Job Name |  |  |  | Address
Fuel |  |  |  | Nat Gas | Propane | Diesel
Service Size
Net Square Footage
GENERAL LOADS | Quantity (or Sq Ft) | Rating (Load) VA | Factor | Loads (VA) |  | Loads (kW) (VA/1,000)
General Lighting and General Use Receptacles @ 3 va / Sq ft | 4000 | 3 VA/Sq ft | 100% | 12000 |  | 12
Small Appliance Circuits (20 Amp) | 2 | 1500 | 100% | 3000 |  | 3 | Hot Tub
Laundry Circuit | 1 | 1500 | 100% | 1500 |  | 1.5 | Sauna
Fixed Appliances: (estimates only, verify with name plate data) | [6 empty] | Welder
Sump Pump | 1 | 500 | 100% | 500 |  | 0.5 | Compressor
Freezer or Refrigerator |  | 750 | 100% | 0 |  | 0 | Range
Microwave | 1 | 1500 | 100% | 1500 |  | 1.5 | Wall Mounted Oven
Disposal |  | 500 | 100% | 0 |  | 0 | Counter Mounted Cooking Surface
Dishwasher | 1 | 1500 | 100% | 1500 |  | 1.5 | Water Heater
Range |  | 5000 | 100% | 0 |  | 0 | Clothes Dryer
Wall Mounted Oven | 2 | 5000 | 100% | 10000 |  | 10 | 1 Ton (verify name plate) (typical FLA 5)
Counter Mounted Cooking Surface |  | 6000 | 100% | 0 |  | 0 | 2 Ton (verify name plate) (typical FLA 10)
Water Heater | 1 | 4500 | 100% | 4500 |  | 4.5 | 3 Ton (verify name plate) (typical FLA 15)
Clothes Dryer | 2 | 5500 | 100% | 11000 |  | 11 | 4 Ton (verify name plate) (typical FLA 20)
Garage Door Opener |  | 500 | 100% | 0 |  | 0 | 5 Ton (verify name plate) (typical FLA 25)
Septic Grinder |  | 750 | 100% | 0 |  | 0 | Compressor (If not included as A/C above)
Well 1/2 HP |  | 1200 | 100% | 0 |  | 0 | Supplimental Electric Heat (= KW times 1000)
Well 3/4 HP |  | 1750 | 100% | 0 |  | 0
Well 1 HP |  | 2350 | 100% | 0 |  | 0
Oil or Gas Furnace |  | 500 | 100% | 0 |  | 0
UPS |  | 500 | 100% | 0 |  | 0
Other: (list by name plate data)
Hot Tub |  | 10000 | 100% | 0 |  | 0
Sauna |  | 5000 | 100% | 0 |  | 0
Welder |  | 2000 | 100% | 0 |  | 0
Compressor |  | 2000 | 100% | 0 |  | 0
|  |  | 100% | 0 |  | 0
|  |  | 100% | 0 |  | 0
TOTAL GENERAL LOADS |  |  |  | 45500 | VA KW | 45.5
HEAT AND A/C LOADS
1. A/C Cooling (If multiple units enter all units)
1 Ton (verify name plate) (typical FLA 5) |  | 1000 | 100% | 0 |  | 0
2 Ton (verify name plate) (typical FLA 10) |  | 2000 | 100% | 0 |  | 0
3 Ton (verify name plate) (typical FLA 15) |  | 3000 | 100% | 0 |  | 0
4 Ton (verify name plate) (typical FLA 20) |  | 4000 | 100% | 0 |  | 0
5 Ton (verify name plate) (typical FLA 25) | 0 | 5000 | 100% | 0 |  | 0
2. Heat Pump(If multiple units enter all units)
Compressor (If not included as A/C above) |  |  | 100% | 0 |  | 0
Supplimental Electric Heat (= KW times 1000) | 0 |  | 100% | 0 |  | 0
3. Electric Heating (Typically @ 250 watts per foot, enter total feet) | Total Feet
Total Feet - Less than 4 separately controlled units | 0 | 250 | 65% | 0 |  | 0
Total Feet - 4 or more separatley controlled units |  | 250 | 40% | 0
TOTAL HEAT AND A/C LOADS |  |  |  | 0 | VA KW | 0
SUMMARY:
General Loads
1st 10 kW of General Loads | 100% | 10 | KW
Remaining General Loads | 40% | 14.2 | KW
CALCULATED GENERAL LOADS |  | 24.2 | KW
HEAT - A/C LOADS |  | 0 | KW
TOTAL CALCULATED LOAD |  | 24.2 | KW
MANAGED LOADS
Loads (kW) (VA/1,000)
0
0
0
0
0
0
TOTAL | 0
WARNING!! VA OF ALL LOADS ARE ESTIMATES OF AVERAGE DEVICES, VERIFY ALL NAMEPLATE DATA!!!
Any Questions Concerning the Use of This Spreadsheet Call United Inspection Agency 215-542-9977

## LOAD SHED
WORKSHEET - NEC 2008, 220 PART IV
Contractor |  |  |  | E-mail
Phone |  |  |  | Fax
Job Name |  |  |  | Address
Fuel |  |  |  | Nat Gas | Propane | Diesel
Service Size
Net Square Footage
GENERAL LOADS | Quantity (or Sq Ft) | Rating (Load) VA | Factor | Loads (VA) |  | Loads (kW) (VA/1,000)
General Lighting and General Use Receptacles @ 3 va / Sq ft |  | 3 VA/Sq ft | 100% | 0 |  | 0
Small Appliance Circuits (20 Amp) |  | 1500 | 100% | 0 |  | 0
Laundry Circuit |  | 1500 | 100% | 0 |  | 0
Fixed Appliances: (estimates only, verify with name plate data)
Sump Pump |  | 500 | 100% | 0 |  | 0
Freezer or Refrigerator |  | 750 | 100% | 0 |  | 0
Microwave |  | 1500 | 100% | 0 |  | 0
Disposal |  | 500 | 100% | 0 |  | 0
Dishwasher |  | 1500 | 100% | 0 |  | 0
Range |  | 5000 | 100% | 0 |  | 0
Wall Mounted Oven |  | 5000 | 100% | 0 |  | 0
Counter Mounted Cooking Surface |  | 6000 | 100% | 0 |  | 0
Water Heater |  | 4500 | 100% | 0 |  | 0
Clothes Dryer |  | 5500 | 100% | 0 |  | 0
Garage Door Opener |  | 500 | 100% | 0 |  | 0
Septic Grinder |  | 750 | 100% | 0 |  | 0
Well 1/2 HP |  | 1200 | 100% | 0 |  | 0
Well 3/4 HP |  | 1750 | 100% | 0 |  | 0
Well 1 HP |  | 2350 | 100% | 0 |  | 0
Oil or Gas Furnace |  | 500 | 100% | 0 |  | 0
UPS |  | 500 | 100% | 0 |  | 0
Other: (list by name plate data)
Hot Tub |  | 10000 | 100% | 0 |  | 0
Sauna |  |  | 100% | 0 |  | 0
Welder |  | 2000 | 100% | 0 |  | 0
Compressor |  | 2000 | 100% | 0 |  | 0
|  |  | 100% | 0 |  | 0
|  |  | 100% | 0 |  | 0
TOTAL GENERAL LOADS |  |  |  | 0 | VA KW | 0
HEAT AND A/C LOADS
1. A/C Cooling (If multiple units only enter the largest)
1 Ton (verify name plate) (typical FLA 5) |  | 1000 | 100% | 0 |  | 0
2 Ton (verify name plate) (typical FLA 10) |  | 2000 | 100% | 0 |  | 0
3 Ton (verify name plate) (typical FLA 15) |  | 3000 | 100% | 0 |  | 0
4 Ton (verify name plate) (typical FLA 20) |  | 4000 | 100% | 0 |  | 0
5 Ton (verify name plate) (typical FLA 25) |  | 5000 | 100% | 0 |  | 0
2. Heat Pump(If multiple units only enter the largest)
Compressor (If not included as A/C above) |  |  | 100% | 0 |  | 0
Supplimental Electric Heat (= KW times 1000) |  |  | 100% | 0 |  | 0
3. Electric Heating (Typically @ 250 watts per foot, enter total feet) | Total Feet
Total Feet - Less than 4 separately controlled units |  | 250 | 65% | 0 |  | 0
Total Feet - 4 or more separatley controlled units |  | 250 | 40% | 0
TOTAL HEAT AND A/C LOADS |  |  |  | 0 | VA KW | 0
SUMMARY:
General Loads
1st 10 kW of General Loads | 100% | 10 | KW
Remaining General Loads | 40% | -4 | KW
CALCULATED GENERAL LOADS |  | 6 | KW
HEAT - A/C LOADS |  | 0 | KW
TOTAL CALCULATED LOAD |  | 6 | KW
WARNING!! VA OF ALL LOADS ARE ESTIMATES OF AVERAGE DEVICES, VERIFY ALL NAMEPLATE DATA!!!